|  | BEAMA | (3) | (e) | Editorial | Better wording to be used: ‘electric portable local space heater’ means an electric local space heater that is equipped with a supply cord and plug by the manufacturer and isdesigned to be portable in order to be operated in different rooms or locations. A portable appliance with features which can be used to fix it to a wall and/or floor is considered an electric fixed local space heater | ‘electric portable local space heater’ means an electric local space heater that is equipped with a supply cord and plug by the manufacturer and is designed to be portable in order to be operated in different rooms or locations. A portable appliance with features which can be used to fix it to a wall and/or floor is considered an electric fixed local space heater |
| --- | --- | --- | --- | --- | --- | --- |
|  | BEAMA | (6) | (a)(vi) | Editorial | A typo needs to be rectified, the efficiency value should be 46.1% and not 41.6%. | The text should be replaced by the below: “seasonal space heating energy efficiency of electric storage local space heaters shall not be less than 46.1 %” |
|  | BEAMA | (6) | (c)(1) | Technical | The below is not necessary for products which have controls already incorporated, as this will cause significant additional burden for manufacturers. - for products that incorporate the controls: ‘This product contains the controls necessary for use and installation in accordance with the ecodesign requirements’ | Remove this clause. |
|  | BEAMA | (6) | (c)(2) | Technical | The proposed text (copied below) would not cover electric local space heaters as these products are out of scope of energy labelling. Alternative text proposed. ‘This product is a [insert product category] and needs to be installed with a separate control in order to function. The control needs as a minimum the following functions: [list of functions necessary to comply with the ecodesign requirements] to achieve the energy efficiency class claimed on the energy label.’; | Replace by the text below: ‘This product is a [insert product category] and needs to be installed with a separate control in order to function. The control needs as a minimum the following functions: [list of functions necessary to comply with the ecodesign requirements] to be compliant with the minimum requirement of the seasonal space heating efficiency for electrical local space heaters or to achieve the energy efficiency class claimed on the energy label.’; |
|  | BEAMA | (6) | (c)(2) | Technical | An additional statement should be added to clarify the basis for the CE declaration. | Add the following statement: The CE declaration and the data claimed in the data sheet for the energy efficiency is based on the control(s) provided by the manufacturer. |
|  | BEAMA | (6) | (d) | Editorial | It should be clarified that this requirement would only apply to controls sold separately to local space heaters. | Replace by the following test: From 1 January 2022 the following product information for all the controls for local space heaters which are sold separately shall be provided |
|  | BEAMA | (6) | (d) | Technical | It should be considered that local space heaters could be paired with controls coming from someone other than the manufacturer of the local space heater. Therefore, heating controls manufacturers should be consulted before going ahead with this requirement, as they would have otherwise not have had any involvement in the review of Lot 20. This requirement would make any heating controls manufacturer have to include information on any product e.g. thermostat that might be sold with a local space heater. It is unlikely that heating controls manufacturers are able to foresee what local space heater their products are compatible with as they would not have knowledge of the specific local space heater; the listing of functions is perhaps a more adequate requirement. This is being done in a completely different way to Lot 1 (for which they already have information requirements). Lot 1 has a specific section “responsibilities for manufacturers of temperature controls” that basically adds information requirements to manufacturers that were previously out of scope. | Information requirements for heating controls should be reconsidered, in a way that is consistent with Lot 1. |
|  | BEAMA | (7) | (d) | Editorial | Correction factor F(2) table should have a column for visible glowing radiant local space heaters, which are still within scope. | Add a column to table for visible glowing radiant local space heaters. |
|  | BEAMA | (7) | (e) | Editorial | Correction factor F(3) table should have a column for visible glowing radiant local space heaters, which are still within scope. | Add a column to table for visible glowing radiant local space heaters. |
|  | BEAMA | (7) | (f) | Technical | The parameters eloff and elidle are not defined. We may wish to provide comments on this once these terms have been defined. | Define eloff and elidle. |
|  | BEAMA | Article 2 |  | Technical | At the stakeholder meeting it was suggested to move implementation away from January, which is in the middle of the heating season. | A change to the implementation date should be considered so that it doesn’t coincide with the middle of the heating season. |